## Points
HMI DNP | Description | State 0 | State 1 | Alarm State | Page Name | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
0 | 230 kV BREAKER B7 | OPEN | CLOSE | 0 | Breaker/MOAB Status | 0 | 1 | 2 | 3 | 4 | 5 | 38 | 40 | 42 | 44 | 46 | 48 | 50 | 52 | 54 | 56 | 58 | . | . | . | . | . | . | . | .
1 | 230 kV BREAKER B8 | OPEN | CLOSE | 0 | Breaker Alarms | 13 | 14 | 15 | 16 | 17 | 18 | 59 | 60 | 61 | 62 | 63 | 64 | . | . | . | . | . | . | . | . | . | . | . | . | .
2 | 230 kV BREAKER B9 | OPEN | CLOSE | 0 | Transformer Alarms | 19 | 20 | 21 | 22 | 23 | 24 | 31 | 32 | 33 | 34 | . | . | . | . | . | . | . | . | . | . | . | . | . | . | .
3 | 230 kV BREAKER B10 | OPEN | CLOSE | 0 | Comm Alarms | 7 | 36 | 69 | 72 | 73 | 74 | 75 | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | .
4 | 230 kV BREAKER B11 | OPEN | CLOSE | 0 | Line Alarms | 26 | 27 | 28 | 29 | 30 | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | .
5 | 230 kV BREAKER B12 | OPEN | CLOSE | 0 | Station Alarms | 9 | 10 | 25 | 35 | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | .
6 | SPARE 32 |  |  | 0 | Relay Alarms | bar: 1 to 25
7 | RTU SCADA STATUS | LOCAL | REMOTE | 0 | Station Non-Critical Alarms | 11 | 12 | 81 | 82 | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | .
8 | SPARE 65 |  |  | 0 | Relay Comm Alarms | 71 | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | .
9 | STATION BATTERY |  |  | 1 | Meter Comm Alarms | 70 | 76 | 77 | 78 | 79 | 80 | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | . | .
10 | STATION CRITICAL ALARM |  |  | 1 | bar: 1 to 25
11 | STATION NON CRITICAL ALARM (Calc 3) |  |  | 1
12 | 230 kV BUILDING DOOR ALARM |  |  | 1
13 | 230 kV BREAKER B7 CRITICAL ALARM |  |  | 1
14 | 230 kV BREAKER B8 CRITICAL ALARM |  |  | 1
15 | 230 kV BREAKER B9 CRITICAL ALARM |  |  | 1
16 | 230 kV BREAKER B10 CRITICAL ALARM |  |  | 1
17 | 230 kV BREAKER B11 CRITICAL ALARM |  |  | 1
18 | 230 kV BREAKER B12 CRITICAL ALARM |  |  | 1
19 | NO 4 XFMR CRITICAL ALARM |  |  | 1
20 | NO 5 XFMR CRITICAL ALARM |  |  | 1 |  | 9: 1; 10: 2; 11: 3; 12: 4; 13: 5
21 | NO 6 XFMR CRITICAL ALARM (FUTURE) |  |  | 1 |  | 9: 6; 10: 7; 11: 8; 12: 9; 13: 10
22 | NO 4 XFMR LTC OUT-OF-STEP (FUTURE) |  |  | 1 |  | 9: 11; 10: 12; 11: 13; 12: 14; 13: 15
23 | NO 5 XFMR LTC OUT-OF-STEP (FUTURE) |  |  | 1 |  | 9: 16; 10: 17; 11: 18; 12: 19; 13: 20
24 | NO 6 XFMR LTC OUT-OF-STEP (FUTURE) |  |  | 1 |  | 9: 21; 10: 22; 11: 23; 12: 24; 13: 25
25 | DFR OPERATION ALARM |  |  | 1
26 | DTT CHANNEL ALARM (FUTURE) |  |  | 1
27 | LINE CARRIER CHANNEL ALARM (FUTURE) |  |  | 1
28 | DTT TRIP RECEIVED OPERATION (FUTURE) |  |  | 1
29 | CARRIER CHECKBACK ALARM (FUTURE) |  |  | 1
30 | 230 kV BREAKER FAILURE-TO-TRIP ALARM |  |  | 1
31 | PRIMARY TRANS DIFFERENTIAL OPERATION |  |  | 1
32 | OVERALL TRANS DIFFERENTIAL OPERATION |  |  | 1
33 | XFMR LEAD PROTECTION OPERATION |  |  | 1
34 | XFMR GROUND BACKUP OPERATION |  |  | 1
35 | ANNUNCIATOR POWER SUPPLY FAILURE ALARM |  |  | 1
36 | COMMUNICATION PROCESSOR FAILURE |  |  | 1
37 | 230 kV MOAB A1 b | CLOSE | OPEN | 1
38 | 230 kV MOAB A1 a | OPEN | CLOSE | 0
39 | 230 kV MOAB A2 b | CLOSE | OPEN | 1
40 | 230 kV MOAB A2 a | OPEN | CLOSE | 0
41 | 230 kV MOAB A3 b | CLOSE | OPEN | 1
42 | 230 kV MOAB A3 a | OPEN | CLOSE | 0
43 | 230 kV MOAB A38 b | CLOSE | OPEN | 1
44 | 230 kV MOAB A38 a | OPEN | CLOSE | 0
45 | 230 kV MOAB A39 b | CLOSE | OPEN | 1
46 | 230 kV MOAB A39 a | OPEN | CLOSE | 0
47 | 230 kV MOD D30 b | CLOSE | OPEN | 1
48 | 230 kV MOD D30 a | OPEN | CLOSE | 0
49 | 230 kV MOD D31b | CLOSE | OPEN | 1
50 | 230 kV MOD D31 a | OPEN | CLOSE | 0
51 | 230 kV MOD D32 b | CLOSE | OPEN | 1
52 | 230 kV MOD D32 a | OPEN | CLOSE | 0
53 | 230 kV MOD D33 b | CLOSE | OPEN | 1
54 | 230 kV MOD D33 a | OPEN | CLOSE | 0
55 | 230 kV MOD D36 b | CLOSE | OPEN | 1
56 | 230 kV MOD D36 a | OPEN | CLOSE | 0
57 | 230 kV MOD D37 b | CLOSE | OPEN | 1
58 | 230 kV MOD D37 a | OPEN | CLOSE | 0
59 | 230 kV CB B9 GROUND LO OPERATION |  |  | 1
60 | 230 kV CB B9 CT COLUMN GRD LO OPERATION |  |  | 1
61 | 230 kV CB B10 GROUND LO OPERATION |  |  | 1
62 | 230 kV CB B10 CT COLUMN GRD LO OPERATION |  |  | 1
63 | 230 kV CB B12 GROUND LO OPERATION |  |  | 1
64 | 230 kV CB B12 CT COLUMN GRD LO OPERATION |  |  | 1
65 | SPARE 122 |  |  | 0
66 | SPARE 123 |  |  | 0
67 | SPARE 124 |  |  | 0
68 | SPARE 125 |  |  | 0
69 | D20 PERIPHERAL COMM (Calc 1) |  |  | 1
70 | METER COMM (Calc2) |  |  | 1
71 | RELAY COMM WD (Calc 4) |  |  | 1
72 | D20A COMM TROUBLE |  |  | 1
73 | D20S1 COMM TROUBLE |  |  | 1
74 | D20S2 COMM TROUBLE |  |  | 1
75 | D20KR COMM TROUBLE |  |  | 1
76 | NO 4 TRANSFORMER SATEC |  |  | 1
77 | NO 5 TRANSFORMER SATEC |  |  | 1
78 | NO 6 TRANSFORMER SATEC |  |  | 1
79 | SEL 3530 RTAC1 COMM TROUBLE |  |  | 1
80 | SEL 3530 RTAC2 COMM TROUBLE |  |  | 1
81 | Station Non Critical Alarms |  |  | 1
82 | GPS Alarm |  |  | 1